## Motor Load List
"From Field to Table" Motor List
Equipment ID | Quantitiy of motors | kW | HP | V | PH | FLA | MCA | BREAKER | EMERGENCY POWER REQ'D | LOCATION (BUILDING) | PROCESS | CONDUCTOR SPECIFICATIONS (use MCA) | Combined kVA
CONV-UL | 2 | 11.6006 | 10 | 208 | 3Ph | 32.2 | 40.25 | 80.5 | N | GPA (Grain Processing Area) | Unloading conveyor motor | 3 x #10 + bond | 23.2012
AU-UL | 3 | 6.3185 | 5 | 120 | 1Ph | 30.4 | 38 | 76 | N | GPA | Unloading auger | 1 x #10 + bond | 18.9556
CONV-LO | 2 | 11.0962 | 10 | 208 | 3Ph | 30.8 | 38.5 | 77 | N | GPA | Loading conveyor motor | 3 x #10 + bond | 22.1924
AU-LO | 3 | 6.3185 | 5 | 120 | 1Ph | 30.4 | 38 | 76 | N | GPA | Loading auger | 1 x #12 + bond | 18.9556
WASHER | 2 | 26.6043 | 30 | 480 | 3Ph | 32 | 40 | 80 | N | GPA | Washing Process | 3 x #8 + bond | 53.2086
DRYER | 2 | 49.8831 | - | 480 | 3Ph | 60 | 75 | 150 | N | GPA | Drying Process | 3 x #4 + bond | 99.7661
HULL | 2 | 129.9038 | 125 | 600 | 3Ph | 125 | 156.25 | 312.5 | N | GPA | Hulling Process | 3 x #00 + bond | 259.8076
MILL | 2 | 80.0207 | 75 | 600 | 3Ph | 77 | 96.25 | 192.5 | Y | GPA | Milling Process | 3 x #3 + bond | 160.0415
MUA-GPA | 1 | 102.8838 | 100 | 600 | 3Ph | 99 | 123.75 | 247.5 | N | GPA | Air conditioning/Heating System | 3 x #0 + bond | 102.8838
MUA-OFF | 1 | 54.04 | 50 | 600 | 3Ph | 52 | 65 | 130 | N | Office Building | Air conditioning/Heating System | 3 x #6 + bond | 54.04
EX-FAN | 3 | 1.3302 | 3/4 | 120 | 1Ph | 6.4 | 8 | 16 | N | Office Building | Exhaust Fan | 1 x #14 + bond | 3.9906
WATER-OFF | 1 | 11.0962 | 10 | 208 | 3Ph | 30.8 | 38.5 | 77 | N | Office Building | Water Pump | 3 x #20 + bond | 11.0962
Motor ID Info:
Add: "-1" or "-2" to identify quantities of motors EX: CONV-UL-1 (Motor 1) CONV-UL-2 (Motor 2)
BREAKER Info:
Max Breaker = FLA*250 FOR MOTORS ONLY!
Standard Sizes of Breakers (a 241A breaker is not manufactured):
0-100A: 15, 20, 25, 30, 40, 50, 60, 75, 80, 90, 100
> 100A: Start at 100 and increase by increments of 25A (ex: 125, 150, 175, 200, 225 etc.)

## Transformer Chart
"From Field To Table" Transformer Chart
Equipment ID | KVA | V(p) | V(s) | XFMR CONFIG | FLA(p) | MCA(p) | BREAKER (p) | CONDUCTORS (p) | FLA(s) | MCA(s) | CONDUCTORS SPECS (s) | TOTAL CONNECTED LOAD
Transformer Name | kVA Rating | Primary | Secondary | Delta or Wye (Primary & Secondary) | Primary | Primary | Primary | Primary | Secondary | Secondary | Secondary | kW (Primary = Secondary)
Transformer 1 | 150 | 600 | 208 | Delta-Wye | 144.3376 | 180.422 | 200 | 3 x #000 + bond | 416.3584 | 520.448 | 3 x #1000 + bond | 83.32
Transfomer 2 | 300 | 600 | 480 | Delta-Delta | 288.6751 | 360.8439 | 375 | 3 x #500 + bond | 360.8439 | 451.0549 | 3 x #700 + bond | 152.8
Transformer 3 | 9 | 600 | 208 | Delta-Wye | 8.6603 | 10.8253 | 15 | 3 x #14 + bond | 24.9815 | 31.2269 | 3 x #10 + bond | 3.6
Transformer 4 | 30 | 600 | 208 | Delta-Wye | 28.8675 | 36.0844 | 45 | 3 x #8 + bond | 83.2717 | 104.0896 | 3 x #2 + bond | 13
Transformer 5 | 3 | 600 | 208 | Delta-Wye | 2.8868 | 3.6084 | 15 | 3 x #14 + bond | 8.3272 | 10.409 | 3 x #14 + bond | 1.8
Example calculations:
XFMR Primary FLA:
kVA = Vp*Ip*√3
(kVA/Vp)/√3 = Ip => FLA
MCA = FLA*1.25
XFMR Secondary FLA:
kVA = Vs*Is*√3
(kVA/Vs)/√3 = Is => FLA
MCA = FLA*1.25
Standard' Transformer Sizes
0-100kVA: 15, 30, 45, 50, 75, 100
> 100A: Start at 100 and increase by increments of 25A (ex: 125, 150, 175, 200, 225 etc.)

## Lumped Load List
"From Field to Table" Lumped Load List
Equipment ID | Quantitiy of Loads | kW | V | PH | FLA | BREAKER (see below) | EMERGENCY POWER REQ'D | LOCATION (BUILDING) | PROCESS | CONDUCTOR SPECIFICATIONS (conductors must match breaker size) | Combined kVA
General Purpose | 3 | 1.2 | 120 | 1 | 10 | 15 | N | GPA (Grain Processing Area) | Interior and exterior plugs | 1 x #14 + bond | 3.6
General Purpose | 3 | 1.4 | 120 | 1 | 11.6667 | 15 | N | Office Building | Workstations, plugs etc. | 1 x #14 + bond | 4.2
Lighting | 3 | 0.6 | 347 | 1 | 1.7291 | 15 | Y | GPA (Grain Processing Area) | Lighting in building | 1 x #14 + bond | 1.8
Lighting | 3 | 0.6 | 120 | 1 | 5 | 15 | Y | Office Building | Lighting in office | 1 x #14 + bond | 1.8
Office Kitchen | 3 | 1.6 | 120 | 1 | 13.3333 | 20 | N | Office Building | Kitchen area in office building | 1 x #14 + bond | 4.8
To determine breaker size for lumped load:
FLA * 125% = Minimum breaker size
Standard Sizes of Breakers (a 241A breaker is not manufactured):
0-100A: 15, 20, 25, 30, 40, 50, 60, 75, 80, 90, 100
> 100A: Start at 100 and increase by increments of 25A (ex: 125, 150, 175, 200, 225 etc.)
Lumped Load FLA:
Three Phase:
kVA = V*I*√3
Single Phase:
kVA = V*I